# 2025 Consumer Confidence Report

## Water System Information

Water System Name: Palomar Mountain Mutual Water Co., Inc

Report Date: 05/29/2026

Type of Water Source(s) in Use: Groundwater wells

Name and General Location of Source(s): Wells 03 and 05, Pedley Valley, Palomar Mountain, CA

Drinking Water Source Assessment Information: A source water assessment for Well 03 was completed in 2002. The assessment found that the source has few potential contaminating activities in the vicinity. However, it identified storm drain discharge points, surface water, and other water supply wells within 900 feet of the well as potential sources of contamination. Given the close proximity of Well 05 to Well 03, Well 05 is also considered to have the same vulnerabilities. A copy of the complete assessment is available for review at the water system office and at the Division of Drinking Water San Diego District Office.

Time and Place of Regularly Scheduled Board Meetings for Public Participation: Second Saturday of the month at 9:00 AM, at 22212 Crestline Rd, Palomar Mountain, CA 92060

For More Information, Contact: Renee Forero-Cook, General Manager at (760) 742-3516 or GM@palomarmountainwater.com

## About This Report

We test the drinking water quality for many constituents as required by state and federal regulations.  This report shows the results of our monitoring for the period of January 1 to December 31, 2025, and may include earlier monitoring data. Last year, your tap water met all U.S. EPA and State drinking water health standards. Palomar Mountain Mutual Water Co., Inc vigilantly safeguards its water supplies and once again, we are proud to report another year in which our system did not violate a maximum contaminant level or any other water quality standard.

## Importance of This Report Statement Spanish

Este informe contiene información muy importante sobre su agua para beber. Favor de comunicarse Palomar Mountain Mutual Water Co., Inc a (760) 742-3516 para asistirlo en español.

## Terms Used in This Report

| Term | Definition |
| --- | --- |
| Maximum Contaminant Level (MCL) | The highest level of a contaminant that is allowed in drinking water. Primary MCLs are set as close to the PHGs (or MCLGs) as is economically and technologically feasible. Secondary MCLs are set to protect the odor, taste, and appearance of drinking water. |
| Maximum Contaminant Level Goal (MCLG) | The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs are set by the U.S. Environmental Protection Agency (U.S. EPA). |
| Maximum Residual Disinfectant Level (MRDL) | The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants. |
| Primary Drinking Water Standards (PDWS) | MCLs and MRDLs for contaminants that affect health along with their monitoring and reporting requirements, and water treatment requirements. |
| Public Health Goal (PHG) | The level of a contaminant in drinking water below which there is no known or expected risk to health. PHGs are set by the California Environmental Protection Agency. |
| Regulatory Action Level (AL) | The concentration of a contaminant which, if exceeded, triggers treatment or other requirements that a water system must follow. |
| Secondary Drinking Water Standards (SDWS) | MCLs for contaminants that affect taste, odor, or appearance of the drinking water. Contaminants with SDWSs do not affect the health at the MCL levels. |
| Secondary Maximum Contaminant Level (SMCL) | Aesthetic standards for contaminants that may cause water to look, smell, or taste unpleasant, but are not considered harmful to health at the levels regulated. There are no PHG or MCLG for SMCL. |
| ppm | parts per million or milligrams per liter (mg/L) |
| ppb | parts per billion or micrograms per liter (µg/L) |
| pCi/L | picocuries per liter (a measure of radiation) |
| μS/cm | microSiemens per centimeter (a measure of electrical conductivity) |
| NTU | Nephelometric Turbidity Units (a measure of water clarity) |
| ND | Not Detected at or above the Detection Limit for Reporting Purpose (DLR) |

## Sources of Drinking Water and Contaminants that May Be Present in Source Water

The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells.  As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.

Contaminants that may be present in source water include:

Microbial contaminants, such as viruses and bacteria, that may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.

Inorganic contaminants, such as salts and metals, that can be naturally-occurring or result from urban stormwater runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.

Pesticides and herbicides, that may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses.

Organic chemical contaminants, including synthetic and volatile organic chemicals, that are byproducts of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, agricultural application, and septic systems.

Radioactive contaminants, that can be naturally-occurring or be the result of oil and gas production and mining activities.

## Regulation of Drinking Water and Bottled Water Quality

In order to ensure that tap water is safe to drink, the U.S. EPA and the State Board prescribe regulations that limit the amount of certain contaminants in water provided by public water systems.  The U.S. Food and Drug Administration regulations and California law also establish limits for contaminants in bottled water that provide the same protection for public health.

## About Your Drinking Water Quality

### Drinking Water Contaminants Detected

Tables 1, 2, 3, and 4 list all of the drinking water contaminants that were detected during the most recent sampling for the constituent.  The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk.  The State Board allows us to monitor for certain contaminants less than once per year because the concentrations of these contaminants do not change frequently.  Some of the data, though representative of the water quality, are more than one year old.

Table 1.  Sampling Results Showing the Detection of Lead and Copper

| Lead and Copper | Sample Date | No. of Samples Collected | 90th Percentile Level Detected | No. Sites Exceeding AL | Range of Results | AL | PHG | Typical Source of Contaminant |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Lead (ppb) | 2024 | 10 | 0 | 0 | 0.62-3.0 | 15 | 0.2 | Corrosion of household plumbing systems; Erosion of natural deposits |
| Copper (ppm) | 2024 | 10 | 0.14 | 0 | 0.026-0.24 | 1.3 | 0.3 | Internal corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives |

Table 2.  Sampling Results for Sodium and Hardness

| Chemical or Constituent (and reporting units) | Sample Date | Level Detected (Average) | Range of Detections | MCL | PHG (MCLG) | Typical Source of Contaminant |
| --- | --- | --- | --- | --- | --- | --- |
| Sodium (ppm) | 5/2024 | 13.5 | 13-14 | None | None | Salt present in the water and is generally naturally occurring |
| Hardness (ppm) | 5/2024 | 76 | 66-86 | None | None | Sum of polyvalent cations present in the water, generally magnesium and calcium, and are usually naturally occurring |

Table 3.  Detection of Contaminants with a Primary Drinking Water Standard

| Chemical or Constituent (and reporting units) | Sample Date | Level Detected (Average) | Range of Detections | MCL | PHG (MCLG) | Typical Source of Contaminant |
| --- | --- | --- | --- | --- | --- | --- |
| TTHMs (Total Trihalomethanes) (ppb) | 8/2025 | 10.8 | N/A | 80 | N/A | Byproduct of drinking water disinfection |
| HAA5 (Sum of 5 Haloacetic Acids) (ppb) | 8/2025 | 2.5 | N/A | 60 | N/A | Byproduct of drinking water disinfection |
| Radium-226 (pCi/L) | 2025 | 0.164 | ND-0.66 | 5 | 0.05 | Erosion of natural deposits |
| Radium-228 (pCi/L) | 2025 | 0.142 | ND-0.84 | 5 | 0.019 | Erosion of natural deposits |

Table 4.  Detection of Contaminants with a Secondary Drinking Water Standard

| Chemical or Constituent (and reporting units) | Sample Date | Level Detected (Average) | Range of Detections | SMCL | PHG (MCLG) | Typical Source of Contaminant |
| --- | --- | --- | --- | --- | --- | --- |
| Chloride (ppm) | 5/2024 | 9 | 8-10 | 500 | N/A | Runoff/leaching from natural deposits |
| Conductance (μS/cm) | 5/2024 | 220 | 200-240 | 1600 | N/A | Substances that form ions when in water |
| Iron (ppb) | 5/2024 | 120 | 110-130 | 300 | N/A | Leaching from natural deposits |
| Odor – Threshold (Units) | 5/2024 | 1 | 1 | 3 | N/A | Naturally-occurring organic materials |
| Sulfate (ppm) | 5/2024 | 4.5 | 4.4-4.6 | 500 | N/A | Runoff/leaching from natural deposits |
| Total Dissolved Solids (TDS) (ppm) | 5/2024 | 145 | 140-150 | 1000 | N/A | Runoff/leaching from natural deposits |
| Turbidity (NTU) | 5/2024 | 0.285 | 0.22-0.35 | 5 | N/A | Soil runoff |

### Additional General Information on Drinking Water

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that the water poses a health risk.  More information about contaminants and potential health effects can be obtained by calling the U.S. EPA’s Safe Drinking Water Hotline (1-800-426-4791).

Some people may be more vulnerable to contaminants in drinking water than the general population.  Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections.  These people should seek advice about drinking water from their health care providers.  U.S. EPA/Centers for Disease Control (CDC) guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and other microbial contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).

Lead-Specific Language: Lead can cause serious health problems, especially for pregnant women and young children. Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. Palomar Mountain Mutual Water Co., Inc is responsible for providing high quality drinking water and removing lead pipes, but cannot control the variety of materials used in plumbing components in your home. You share the responsibility for protecting yourself and your family from the lead in your home plumbing. You can take responsibility by identifying and removing lead materials within your home plumbing and taking steps to reduce your family's risk. Before drinking tap water, flush your pipes for several minutes by running your tap, taking a shower, doing laundry or a load of dishes. You can also use a filter certified by an American National Standards Institute accredited certifier to reduce lead in drinking water. If you are concerned about lead in your water and wish to have your water tested, contact Palomar Mountain Mutual Water Co., Inc at GM@palomarmountainwater.com. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available at http://www.epa.gov/safewater/lead.